## Calibration_soc0p_20240109
SOC Working Calibration and Basic Troubleshooting					Date	01/12/24
-	Need more equipment to adust R0, SA, and SB
				Build	g20240109
Equipment
1	Clamping multimeter					Device	soc0p
2	~40W AC Fan
3	Phone BT connect to device, running ‘vv99;’ having built-in software filtering					Battery Type	CH
4	Epoch converter app for UNIX Zulu Time
5	Laptop to power device with system off

Build – First step
1	Dump and save to file from previous install ( Hd; PR; PV; Pf; Q; )					Note DAB		DAB+-	-0.023
2	Build and load from Particle Workbench
3	Consider using the reset command RR;					pre filename		soc0p_pre_g20240109
4	Dump and save to file from new install ( Hd; PR; PV; Pf; Q; )					post filename		soc0p_g20240109
5	Set Time ( UT; )					UT from Pf;	1705080356
6	At first opportunity reset at SAT ( Ri; ) to provide for best DAB +- data collected after install over period of time

Zero Current Calibration

1	Should be done at SAT saturation
2	Power device with laptop or phone
3	Turn off system master power or pull all breakers. Pull PV plug to CC.

4	Note as-is values		DA	0.973		SA	1.006	don’t adjust
			DB	0.15		SB	1.042	don’t adjust		Requirements
			Dc	0.03		Sr	1	caution		Min	Max	Units

5	As-is Observations		Time start	12:42:00 PM	Time end	12:49:00 PM	Duration	00:07:00		5	15	min
	poower		Vb Clamp	14.34		14.35
			Vb	14.325		14.326		Vb Clamp – Vb Range
			Calculate Vb Clamp – Vb and Adjust Dv					0.0139999999999993	0.0250000000000004	Adj Dc
			voc	14.32		14.33		avg=	0.0194999999999999	-0.02	0.02	volts
			voc_soc	14.325		14.327
			Tb	14.69		14.81				Adj DA and DB
	no power		imh	0.02		0.03				-0.1	0.1	A
			inh	0.09		0.12		( +-0.2 for Photon )		-0.1	0.1	A

6	Note final values		DA	0.95		SA	1.006	don’t adjust
	both?		DB	0.067		SB	1.042	don’t adjust
			Dc	0.03		Sr	1	don’t adjust
	doesn’t show on BT		UT ( Pf; )	1705082403					Adjust to UNIX Zulu
			Qinf	-1572					0	after ‘Ri;’

Check for Faults

1	Pf;					Fault free; quiet allowed

Dynamic Test for Randles Coefficient R0 ( Sr; )

1	Restore power. Turn on inverter and 40W fan

			Time start		Time end		Duration			5	15	min
			Vb Clamp					Vb Clamp – Vb Range		Adj Sr
			Vb					-0.1	0.1	volts
			voc
			Ib

2	Note final values. After R0 established, should be very rare to change					Sr				Don’t adjust this unless sure

Curve Test for VOC ( SOC )

1	Discharge to soc < 0.92 ( Q; )

2	Note as-is values					Dw

3	Unplug fuses; leave main power on

4	Note observations		Time start		Time end		Duration			5	15	min
			voc					Voc - voc_soc		Adj Dw
			voc_soc					-0.02	0.02	volts

4	Note final values					Dw

Summary					Requirements
				Min	Max	Units
	Static Vb Clamp – Vb range		0	0	-0.05	0.05	volts
	Dv pre-post		0.03	0.03
	imh		0.02	0.03	-0.1	0.1	A
	inh		0.09	0.12	-0.1	0.1	A
	DA pre-post		0.973	0.95
	DB pre-post		0.15	0.067
	Dyn Vb Clamp – Vb range		0	0	-0.1	0.1	volts
	Sr pre-post
	Dw pre-post		0	0

	SA		1.006	1.006
	SB		1.042	1.042
	Sr		1	0

Troubleshooting

1	wrap faults. This is a comprehensive system health test, affected by all adjustments
	Check DA, DB, SA, SB, Dv, Dw, and Sr

2	cc_diff faults. This is a accumulated system health test. Generally turned off around SAT so when checking, look when <92% SOC
	voc does not equal voc_stat. Check voltage calibrations Dv and Dw

3	Plots show soc differences
	Simulation soc_ver is poor if the update time of Ib is longer than actual. There is a setting to force simulation soc = recorded soc

## Calibration
SOC Working Calibration and Basic Troubleshooting					Date
-	Need more equipment to adust R0, SA, and SB
				Build
Equipment
1	Clamping multimeter					Device
2	~40W AC Fan
3	Phone BT connect to device, running ‘vv99;’ having built-in software filtering					Battery Type
4	Epoch converter app for UNIX Zulu Time
5	Laptop to power device with system off					UT from Pf;

Build – First step
1	Dump and save to file from previous install ( Hd; Pf; Q; )					Note DAB		DAB+-
2	Build and load from Particle Workbench
3	Consider using the reset command RR;					pre filename
4	Dump and save to file from new install ( Hd; Pf; )					post filename
5	Set Time ( UT; )
6	At first opportunity reset at SAT ( Ri; ) to provide for best DAB +- data collected after install over period of time

Zero Current Calibration

1	Should be done at SAT saturation
2	Power device with laptop or phone
3	Turn off system master power or pull all breakers

4	Note as-is values		DA			SA		don’t adjust
			DB			SB		don’t adjust		Requirements
			Dv			Sr		caution		Min	Max	Units

5	As-is Observations		Time start		Time end		Duration			5	15	min
			Vb Clamp
			Vb					Vb Clamp – Vb Range		Adj Dv
			Calculate Vb Clamp – Vb and Adjust Dv					-0.05	0.05	volts
			voc
			voc_soc
			Tb					Adj DA and DB
			imh					-0.1	0.1	A
			inh					( +-0.2 for Photon )		-0.1	0.1	A

6	Note final values		DA			SA	0	don’t adjust
			DB			SB	0	don’t adjust
			Dv			Sr	0	don’t adjust
			UT ( Pf; )					Adjust to UNIX Zulu
			Qinf					0	after ‘Ri;’

Check for Faults

1	Pf;					Fault free; quiet allowed

Dynamic Test for Randles Coefficient R0 ( Sr; )

1	Restore power. Turn on inverter and 40W fan

			Time start		Time end		Duration			5	15	min
			Vb Clamp					Vb Clamp – Vb Range		Adj Sr
			Vb					-0.1	0.1	volts
			voc
			Ib

2	Note final values. After R0 established, should be very rare to change					Sr				Don’t adjust this unless sure

Curve Test for VOC ( SOC )

1	Discharge to soc < 0.92 ( Q; )

2	Note as-is values					Dw

3	Unplug fuses; leave main power on

4	Note observations		Time start		Time end		Duration			5	15	min
			voc					Voc - voc_soc		Adj Dw
			voc_soc					-0.02	0.02	volts

4	Note final values					Dw

Summary					Requirements
				Min	Max	Units
	Static Vb Clamp – Vb range		0	0	-0.05	0.05	volts
	Dv pre-post		0	0
	imh		0	0	-0.1	0.1	A
	inh		0	0	-0.1	0.1	A
	DA pre-post		0	0
	DB pre-post		0	0
	Dyn Vb Clamp – Vb range		0	0	-0.1	0.1	volts
	Sr pre-post
	Dw pre-post		0	0

	SA		0	0
	SB		0	0
	Sr		0	0

Troubleshooting

1	wrap faults. This is a comprehensive system health test, affected by all adjustments
	Check DA, DB, SA, SB, Dv, Dw, and Sr

2	cc_diff faults. This is a accumulated system health test. Generally turned off around SAT so when checking, look when <92% SOC
	voc does not equal voc_stat. Check voltage calibrations Dv and Dw

3	Plots show soc differences
	Simulation soc_ver is poor if the update time of Ib is longer than actual. There is a setting to force simulation soc = recorded soc

## Build Load Workbench
Build and Load Particle Workbench Image to Device

1	Install Workbench (web-based toolchain)
	Start by logging in to https://docs.particle.io/quickstart/workbench

2	Install GitHub (web-based toolchain)
	sign in online. clone myStateOfCharge

2	In local_config.h
	- select device
	- compile

## GUI test
jetbrains - pycharm community

## Create New Release
Create New Release

1	Complete GUI testing all platforms
	- look in G:\My Drive\GitHubArchive\SOC_Particle\dataReduction\<previous release>
	- verify presence of all .csv files

2	Turn off all special debug defines in local_config.h.<>.h files, e.g. DEBUG_QUEUE, DEBUG_INIT, LOGHANDLE

3	Commit and Push edits
	- create 'tag' named with new branch name so can find it later if needed
	- GitHub - History - <select latest commit> - right-click – Create Tag - <new branch name>
	- OK if cleanup produces some new changes / history after Create Tag. They'll be rolled into new branch at next step

4	Create new branch
	- Current branch – New branch
	- g<date><optional subversion letter>			e.g. g20231111
	- go to GitHub on web and change 'Default branch' to the new branch
	----signing in will fix most problems!

5	Finalize
	- Update version in version.h
	- Sign into all laptops used to administer devices and change branch and build images for all devices
	----Particle: clean application (local) is your friend